MODBUS SCANNER+ECY

POINT POPULATOR

Version 1.0.0

User Guide & Quick Start Modbus TCP device scanner with automated Eclypse point population

ModbusScanner+ECYPointPopulator1.0.0.exe

Requires Windows 10/11  •  PowerShell 5.1  •  .NET 4.7+

# Quick Start Guide

Get from zero to a fully populated Eclypse point list in under five minutes.

## Step 1 — Launch the Application

- Double-click Modbus Scanner+ECY point populator 1.0.0.exe. No installation required.

- The application opens maximised with the left control panel and the register map on the right.

- The Debug Log panel at the bottom is collapsed by default — click the DEBUG LOG bar to expand it.

NOTE Run as Administrator if your network adapter requires elevated permissions to open raw sockets.

## Step 2 — Connect to Your Modbus Device

- In the CONNECTION section, enter the device IP address, port (default 502), Unit ID, and timeout.

- Enter a Device Name — this becomes the Eclypse device identifier (default: ModbusScanner).

- Click Connect. The status dot in the bottom bar turns green on success.

- If the connection fails, use Network Diagnostic to confirm TCP reachability before troubleshooting further.

## Step 3 — Configure Register Counts

- Expand KNOWN REGISTER COUNTS and set the quantity for each FC type that your device supports.

- FC01 Coils and FC02 Discrete Inputs — set to number of bits.

- FC03 Holding Registers and FC04 Input Registers — set to number of word registers.

## Step 4 — Scan

- Expand SCAN PARAMETERS and choose the register type (ALL scans all four FC types in sequence).

- Set Start Address (zero-based) — leave at 0 to start from the first register.

- Leave Poll Interval at 0 for a single shot scan, or enter a value in milliseconds for continuous polling.

- Click Scan. The register map populates with live values.

TIP Set Poll Interval to 1000 (1 second) to watch values update in real time. Click Stop Poll to halt.

## Step 5 — Label Your Points (Optional)

- Click any cell in the NAME column to type a friendly label for that register.

- Click any cell in the DATA TYPE column to change value interpretation (UINT16, INT16, FLOAT32, etc.).

- Use + Add Row in the register map header to manually add points that were not scanned.

## Step 6 — Post to Eclypse

- Expand POST DEVICE TO API. Enter your Eclypse base URL, username, and password.

- Click Preview JSON + POST Device to create the Modbus device on the Eclypse controller.

- Once the device is created (HTTP 201), click Preview JSON + POST Points to populate all register map entries as Eclypse points.

- Watch the Debug Log for HTTP response codes and any error details.

NOTE Both POST operations open a preview window so you can inspect and edit the JSON body before sending.

# Interface Overview

The application window is divided into three areas: the left control panel, the register map, and the debug log.

## Left Control Panel

Each section header is clickable — click to expand or collapse. The arrow indicator shows v (expanded) or > (collapsed).

| Section | Default State | Purpose |
| --- | --- | --- |
| CONNECTION | Expanded | IP address, port, Unit ID, timeout, device name, connect/disconnect buttons |
| SCAN PARAMETERS | Expanded | Register type selector, start address, poll interval, Scan and Stop Poll buttons |
| KNOWN REGISTER COUNTS | Collapsed | Per-FC quantity limits — set these to match your device exactly |
| WRITE REGISTER | Collapsed | Single-register write using FC05 (coil) or FC06 (holding register) |
| POST DEVICE TO API | Expanded | Eclypse API URL, credentials, and POST buttons for device and points |
| TOOLS | Collapsed | Export CSV, Import CSV, Save Log, Clear All |

## Register Map

Displays all scanned registers. Columns:

| Column | Editable | Description |
| --- | --- | --- |
| ADDRESS | No | Modbus reference address (00001, 10001, 30001, 40001 etc.) |
| REG TYPE | No | FC type: Coil, Discrete Input, Holding Register, or Input Register |
| DATA TYPE | Yes | Click to change value interpretation: UINT16, INT16, FLOAT32, FLOAT64, INT32, UINT32, BOOL, BIT, HEX, BINARY |
| VALUE | No | Current decoded value. Updates every poll cycle. |
| NAME / LABEL | Yes | Click to type a friendly name. Used as the Eclypse point key on POST. |
| CHANGED | No | Flags registers whose value changed since last scan. |

Right-click any row for: Remove Row, Copy Value, Copy Modbus Address.

## Add Row Panel

Click + Add Row in the register map header to reveal the inline entry bar. Fill in:

- NAME (optional) — friendly label for the point.

- MODBUS ADDRESS — full Modbus reference, e.g. 40001 for the first holding register.

- REGISTER TYPE — select the FC type from the dropdown.

- DATA TYPE — select the value interpretation.

Click Add (green) to append the row. Click Cancel or the – Cancel header button to dismiss without adding.

## Debug Log

Click the DEBUG LOG bar at the bottom to expand the log panel. All Modbus communication is logged here in detail, including:

- Full MBAP header fields (Transaction ID, Protocol ID, Length, Unit ID)

- Raw hex bytes for every TX and RX frame — identical to a Wireshark capture

- PDU decode: FC code, address, quantity, and all register/bit values

- Round-trip time for each request

- HTTP request and response details for all API operations

- Exception code descriptions for Modbus errors

TIP Enable Debug Mode via the checkbox in the title bar to see all MBAP and hex-level entries. Disable it to see only high-level status messages.

# Features Reference

## Modbus Scanning

- ALL mode — scans FC01, FC02, FC03, and FC04 in sequence using the counts set in Known Register Counts.

- Single FC mode — scans only the selected function code.

- Poll mode — set Poll Interval in milliseconds to continuously re-scan. Changed values are flagged in the CHANGED column.

- Start Address — zero-based. Address 0 = Modbus reference 1 (40001 for FC03).

## Data Type Interpretation

The DATA TYPE column controls how the raw 16-bit register value is displayed:

| Data Type | Description |
| --- | --- |
| UINT16 | Unsigned 16-bit integer (0 to 65535) — default for word registers |
| INT16 | Signed 16-bit integer (-32768 to 32767) |
| UINT32 | Unsigned 32-bit — combines two consecutive registers (hi:lo) |
| INT32 | Signed 32-bit — combines two consecutive registers |
| FLOAT32 | IEEE 754 single-precision float — combines two consecutive registers |
| FLOAT64 | IEEE 754 double-precision float — combines four consecutive registers |
| BOOL | True if register value is non-zero |
| BIT | Single bit representation |
| HEX | Hexadecimal display (e.g. 0x004B) |
| BINARY | Binary bit pattern (e.g. 0000000001001011) |

## Manual Register Entry

Use + Add Row to manually add any register to the map without scanning. This is useful when:

- You know a register address but the device is not connected yet

- You want to pre-label a point before scanning

- You are building an Eclypse point list from a device datasheet

Manually added rows appear with value 0 (manual) and are included in the points POST.

## Write Register

Expand WRITE REGISTER to send single write commands:

- FC05 — Write Single Coil: writes ON (0xFF00) or OFF (0x0000) to a coil address.

- FC06 — Write Single Register: writes a 16-bit value to a holding register address.

The Write button is enabled only when connected.

## Network Diagnostic

Click Network Diagnostic in the CONNECTION section to run a TCP reachability test:

- ICMP ping with round-trip time

- TCP port probe with connect time

- DNS resolution check

Results are shown in the Debug Log.

## CSV Import and Export

- Export CSV — saves the current register map as a .csv file with columns: MbAddress, RegType, DataType, Value, Name, Changed.

- Import CSV — loads a .csv file and replaces the current register map. Accepts flexible column name variants (see table below).

Supported CSV column name variants for import:

| Field | Accepted Column Names |
| --- | --- |
| Address | MbAddress, Address |
| Register Type | RegType — values: Coils, DiscreteInput, HoldingRegister, InputRegister, FC01–FC04, Coil, Discrete, Holding, Input, or full display names |
| Data Type | DataType — any casing accepted (UINT16, Uint16, uint16 all valid) |
| Value | Value — numeric prefix extracted automatically |
| Name | Name |

NOTE Importing replaces the entire register map. A confirmation dialog shows the row count before committing.

## POST Device to Eclypse

Generates and posts the Modbus device JSON to the Eclypse REST API.

- Endpoint: POST {baseUrl}/{DeviceName}

- Preview window: shows the full JSON body and authorization header. Edit directly before sending if needed.

- Auth modes: Plain Basic (username:password base64), SHA-256 Basic (username:sha256hash base64), or Custom raw header.

- A successful POST returns HTTP 201 Created.

## POST Points to Eclypse

Translates the entire register map into Eclypse point JSON and posts it.

- Each row becomes one point entry keyed by Name (if set) or point_{MbAddress}

- Coils and Discrete Inputs use data-type Bit with boolean present-value and priority-array

- Holding and Input Registers use the DataType column value with integer present-value

- priority-array[15] is set to the current scanned value if non-zero, otherwise null

- The status block is intentionally omitted — the Eclypse controller populates it server-side

IMPORTANT Post the device first (Step 6a) before posting points. The points endpoint requires the device to already exist at the target URL.

# Troubleshooting

| Symptom | Likely Cause | Resolution |
| --- | --- | --- |
| Cannot connect | Wrong IP, port, or firewall block | Run Network Diagnostic. Confirm port 502 is open. Check Unit ID. |
| Scan returns zeros for all registers | Quantity set too high | Set Known Register Counts to match device datasheet exactly. |
| Modbus Exception Code 2 | Address out of range | Reduce start address or quantity. Verify with device documentation. |
| Modbus Exception Code 1 | FC not supported | Device may not support that function code. Try a different FC. |
| HTTP 400 on POST Points | Invalid JSON field or type mismatch | Check the JSON preview window. Verify register types and data types. |
| HTTP 401 on POST | Wrong credentials or auth mode | Confirm username/password. Try switching auth mode to SHA-256. |
| HTTP 409 on POST Device | Device name already exists | Change the Device Name in the CONNECTION section or delete the existing device on the Eclypse. |
| Values show as incorrect numbers | Wrong Data Type selected | Click the DATA TYPE cell and select the correct interpretation. |
| Import CSV fails | Missing required columns | Ensure CSV has at minimum MbAddress (or Address) and RegType columns. |
| Window does not open | STA mode not set | Launch with: powershell -STA -File ModbusScanner.ps1 |

# Modbus Address Reference

Modbus uses a five-digit addressing convention. The application displays and uses these references throughout.

| FC Code | Register Type | Address Range |
| --- | --- | --- |
| FC01 | Coils (read/write bits) | 00001 – 09999 |
| FC02 | Discrete Inputs (read-only bits) | 10001 – 19999 |
| FC03 | Holding Registers (read/write words) | 40001 – 49999 |
| FC04 | Input Registers (read-only words) | 30001 – 39999 |

## Modbus TCP Frame Structure

The Debug Log shows every frame field. For reference:

| MBAP Field | Description |
| --- | --- |
| Transaction ID (2 bytes) | Incremented per request. Response must echo the same value. |
| Protocol ID (2 bytes) | Always 0x0000 for Modbus. |
| Length (2 bytes) | Number of bytes that follow (Unit ID + PDU). |
| Unit ID (1 byte) | Slave/device address within a gateway. Use 1 for direct TCP connections. |
| Function Code (1 byte) | Defines the operation. 0x80 OR'd with the FC indicates an exception response. |
| Data (variable) | Address, quantity, and register values depending on the function code. |

## Eclypse API Requirements

- Base URL format: https://{controller-ip}/api/rest/v2/services/modbus/devices

- TLS 1.2 enforced. Certificate validation is disabled by default for self-signed controllers.

- POST Device: creates the Modbus device entry. Returns 201 on success.

- POST Points: appended to the device URL as /{DeviceName}/points. Returns 201 on success.

- Authentication: Basic Auth with either plaintext password or SHA-256 hashed password, base64-encoded.

## Keyboard Shortcuts

| Action | Shortcut |
| --- | --- |
| Edit Name cell | Click the NAME cell, then type |
| Confirm cell edit | Enter or Tab |
| Cancel cell edit | Escape |
| Copy from register map | Right-click > Copy Value or Copy Modbus Address |
| Remove row | Right-click > Remove Row |